## Engineering
Estates Asset Management: Property Appraisal Manual
|  |  | Appendix 7 - GP Schedule of Rates - Statutory - Engineering Items 1Q 2023 | [6 empty] | Version 1.3 October 2023
[6 empty] | Cost |  |  |  | Risk Rating
Element | Element | Sub Element | Sub Element | Item | Unit (if appropriate) | Small - i.e. < 500.00m2 | Medium - i.e. 500.00 to 999.99m2 | Large - i.e. 1,000.00m2 + | Additional Comments | Consequence | Likelihood | Total Risk
4 | Lifting Operations and Lifting Equipment (LOLER) Regulations 1998 (incorporating SHTM, 08-02 Lifts) | 4.99 | Other | Provide a LOLER thorough examination report for all lifting equipment. | No. | 1928 |  |  | Examination report required for passenger lifts, goods lifts and dumb waiters. Where no report exists and lift equipment is beyond its recommended lifespan, then include for replacement as per rates in 15.00. Engineering report (15.01 to 15.99) must also be updated to reflect this, i.e. where originally you had the lifts at say B and 5 years remaining life, and now include them under statutory, you will need to amend the Engineering to a B and the life cycle period for remaining life, plus a comment stating "lifts being replaced under Statutory" | 4 | 2 | 8
21 | Firecode, Alarm and Detection Systems (incorporating SHTM 82) | 21.01 | Alarm and Detection | Annual inspection and testing of all fire alarm and detection equipment. | No. | 324 | 644 | 965 |  | 4 | 2 | 8
|  | 21.01 | Alarm and Detection | Bring existing installation up to a minimum L3 standard in compliance with SHTM's for all health care properties. | m2 | 44 |  |  | Engineering report (19.01 to 19.02) must also be updated to reflect this, i.e. where originally you had the fire alarm panel and wiring at say B and 5 years remaining life, and now include them under statutory, you will need to amend the Engineering to a B and the life cycle period for remaining life, plus a comment stating "fire alarms being upgraded under Statutory" | 4 | 2 | 8
24 | Firecode - General (inc SHTM 80-86 excl SHTM 82 | 24.02 | Escape Lighting | Provide adequate emergency lighting on all escape routes. | m2 | 32 |  |  |  | 4 | 2 | 8
|  | 24.02 | Escape Lighting | Provide annual emergency lighting test certificate. | No. | 644 | 1287 | 1928 |  | 4 | 2 | 8
|  | 24.03 | Signage | Provide adequate exit signage on all escape routes. | No. | 324 | 644 | 965 |  | 4 | 2 | 8
|  | 24.05 | Sprinklers / Automatic Fire Extinguisher System | Annual inspection and testing of all automatic fire suppression systems. | No. | 644 | 1287 | 1928 |  | 4 | 2 | 8
|  | 24.08 | Lightning Conductors | Annual inspection and testing of all lightning protection installations. | No. | 965 | 1287 | 1928 |  | 4 | 2 | 8
29 | Gas Safety (Installation and Use) Regulations 1998 | 29.99 | Other | Provide annual 'Gas Safe' certificate for all gas-fired plant and equipment. | No. | 644 | 965 | 1287 |  | 4 | 2 | 8
34 | Infection Control - HAI Level 4 | 34.04 | Provision of Facilities for Decontamination | N/A | [7 empty] | 0
41 | Pressure Systems 2014 | 41.01 | Written Scheme of Examination | N/A |  |  |  |  | No systems in excess of 250 bar / litres anticipated in this survey programme. |  |  | 0
|  | 41.02 | Automatic Controls | N/A | [7 empty] | 0
|  | 41.03 | Pressure Alarms | N/A | [7 empty] | 0
|  | 41.04 | Fire Proofing of Rooms | N/A | [7 empty] | 0
|  | 41.05 | Safe Discharge Area | N/A | [7 empty] | 0
|  | 41.06 | Schematic Diagrams | N/A | [7 empty] | 0
|  | 41.99 | Other | N/A | [7 empty] | 0
42 | Water 2014 (incorporating SHTM 04-01 and HSE Guidance Document HSG 274 Part 1 to 3 & L8) & SHTM 03-02: Heat Emitters | 42.01 | Supply | N/A |  |  |  |  | Individual checks should be carried out as part of the legionella risk assessment. |  |  | 0
|  | 42.02 | CW Tank Storage & Distribution | Ensure cold water storage tank is fitted with an overflow screen and screened vent, has a rigid close-fitting lid and inlet and outlet connections are on opposite ends to encourage water flow across the tank. | No. | 1287 | 1928 | 2571 |  | 4 | 2 | 8
|  | 42.03 | Flushing Provision | Flush hot and cold outlets daily. | No. | 644 | 965 | 1287 |  | 4 | 2 | 8
|  | 42.04 | CW Outlet Temperature | Test cold water outlets weekly and ensure cold water delivery temperature is below 20°C. | No. | 965 | 1287 | 1928 |  | 4 | 2 | 8
|  | 42.05 | HW Tank Storage & Distribution | Ensure hot water is stored at least at 60°C. | No. | 644 | 965 | 1287 |  | 4 | 2 | 8
|  | 42.06 | Calorifier Storage & Flow Temperature | Refer to item 42.05. | [5 empty] | 4 | 2 | 8
|  | 42.07 | Continuous Distribution Temperature | Provide secondary return circuit and pump where necessary to ensure hot water delivery times < 2 mins. | No. | 3210 | 6418 | 9626 |  | 4 | 2 | 8
|  | 42.08 | HW Outlet Temperature | Test cold water outlets weekly and ensure hot water delivery temperature is above 50°C. | No. | 1287 | 1928 | 2571 |  | 4 | 2 | 8
|  | 42.09 | Blended Water Pipework | Ensure maximum run of blended hot water pipework is such that the required mixed temperature, at the furthest outlet, should be reached within 30 seconds. | No. | 644 | 1287 | 2571 |  | 4 | 2 | 8
|  | 42.1 | Dead Legs | Remove dead legs from water distribution pipework. | No. | 644 | 1287 | 1928 |  | 4 | 2 | 8
|  | 42.11 | Circulation Pumps | Refer to item 42.07. | [5 empty] | 4 | 2 | 8
|  | 42.12 | Non-Return Valves | Fit non-return valves to prevent backflow of hot water to the cold feed. | No. | 644 |  |  |  | 4 | 2 | 8
|  | 42.13 | System Flushing Provision | Refer to item 42.03. | [5 empty] | 4 | 2 | 8
|  | 42.14 | Calorifier Open Vent | Ensure open vent is directed into a separate tundish/drain which discharges at a safe and visible point and acts as a warning pipe. Discharge into the cold water storage tank is not advised. | No. | 1287 | 1928 | 2571 |  | 4 | 2 | 8
|  | 42.15 | Calorifier Temperature Control System | Ensure hot water is stored at least at 60°C. | No. | 324 | 644 | 965 |  | 4 | 2 | 8
|  | 42.16 | Temperature Monitoring | Carry out weekly temperature checks of hot and cold water storage systems and hot and cold water outlets on index runs. | No. | 3210 | 4494 | 5776 |  | 4 | 2 | 8
|  | 42.17 | Ductwork System | Carry out regular inspections and cleaning of ductwork systems to minimise legionella risk. | No. | 965 | 1287 | 1928 |  | 4 | 2 | 8
|  | 42.18 | Steam Humidification | N/A | [7 empty] | 0
|  | 42.19 | Water Bylaws | Ensure water installations are compliant with current Water Byelaws. | No. | 1287 | 3210 | 5136 |  | 4 | 2 | 8
|  | 42.2 | Outlet Temperature | Fit thermostatic valves to all outlets not intended for food hygiene and decontamination purposes. | No. | 644 | 965 | 1287 |  | 4 | 2 | 8
|  | 42.21 | Outlet Physical Precautions | Provide thermostatic mixing devices on hot water outlets. Hot water outlets provided for food hygiene and decontamination purposes should be provided with a notice 'Caution - Very Hot Water'. | No. | 1287 | 3210 | 5136 |  | 4 | 2 | 8
|  | 42.22 | Lower Maximum Safe Temperature | Ensure hot water is stored at least at 60°C. | No. | 644 |  |  |  | 4 | 2 | 8
|  | 42.23 | Thermostatic Mixer - Fail Safe | Ensure all TMVs are regularly serviced and fail-safe tested. | No. | 324 | 644 | 965 |  | 4 | 2 | 8
|  | 42.24 | Maximum Surface Temperature (Radiators) | Provide LST radiators in all assisted toilets to prevent accidental scalding. | No. | 1287 | 3210 | 6418 |  | 4 | 2 | 8
|  | 42.25 | Exposed Pipework | Ensure exposed LTHW distribution pipework is insulated to prevent accidental scalding. | m2 | 31 |  |  |  | 4 | 2 | 8
|  | 42.99 | Other | Provide a legionella risk assessment | No. | 1287 | 1928 | 2571 |  | 4 | 2 | 8
44 | Heating and Ventilation 2014 | 44.01 | Ventilation in Healthcare Premises (incorporating SHTM 03-01 Heating and Ventilating Systems Guidance) | Provide adequate ventilation throughout. | m2 | 4.9 |  |  | Includes mechanical ventilation in toilets and all areas without openable windows. | 2 | 2 | 4
|  | 44.01 | Ventilation in Healthcare Premises (incorporating SHTM 03-01 Heating and Ventilating Systems Guidance) | Ensure ventilation grilles and ductwork are clean. | No. | 644 | 965 | 1928 |  | 2 | 2 | 4
|  | 44.99 | Other | [8 empty] | 0
48 | Electrical - Electrical Safety Guidance for Low Voltage (incorporating SHTM 06-01 and 02 Electrical Safety Guidance) | 48.01 | Electrical System protected from unauthorised use | Provide lockable access to all electrical distribution equipment. | No. | 324 |  |  | Where no fixed wiring report exists and the power and / or lighting wiring is beyond its recommended CIBSE lifespan, then include for replacement as per rates in 17.05. Engineering report (17.05) must also be updated to reflect this, i.e. where originally you had the electrical power and lighting wiring at say B and 5 years remaining life, and now include them under statutory, you will need to amend the Engineering to a B and the life cycle period for remaining life, plus a comment stating "wiring being replaced under Statutory" | 4 | 2 | 8
|  | 48.02 | Protected from damage | Provide protection from damage | No. | 644 | [5 empty] | 0
|  | 48.03 | Emergency Lighting | Provide emergency lighting adjacent to all distribution equipment. | No. | 644 | 965 | 1928 |  | 3 | 2 | 6
|  | 48.04 | Signage | Provide poster showing an approved method of treatment for electric shock adjacent to main switchgear. | No. | 33 |  |  |  | 4 | 2 | 8
|  | 48.05 | Earth bonding | Provide earth bonding in accordance with BS 7671 | No. | 1287 | 2571 | 5136 |  | 4 | 2 | 8
|  | 48.99 | Other | Provision of periodic inspection and testing in line with recommendations of BS 7671 | No. | 1287 | 1928 | 2571 |  | 4 | 2 | 8
Version 1.3 October 2023